## Electrical
Date
22-Jan-2018 |  | ELECTRICAL SAFETY
Bangladesh Accord Remediation Summary of Actions Required
Factory Name & Address |  | Sawftex Ltd, Bhangnahati, Sreepur, Gazipur, Dhaka
Date of Inspection by Accord |  | 2014-06-29
Accord Rating
Finance Plan Agreed |  | Yes
Item No | Accord Inspection Observation | Accord Action Plan | Final Action Plan | Final Timeline | Comments from Accord | Accord Timeline | Progress Status
1 | Workers that operate and maintain the electrical system have not received electrical safety training. | Develop and implement an electrical safety program. Include key topics such as lock out tag out procedures, personal protective equipment requirements, etc. | Corrected | 12/05/2015 | On 29/05/2016: Corrected. On 01/09/2016: Found corrected on 1st follow-up. Also found corrected in the second. | 4/24/2015 | Corrected
2 | Distribution boards are metal enclosed with no dead front construction. | Ensure distribution boards are metal enclosed with a dead front construction. | Corrected | 30/06/2015 | On 29/05/2016: Corrected. On 01/09/2016: Found corrected on 1st follow-up. Also found corrected in the second. | 4/24/2015 | Corrected
3 | Underground service cables are laid in non-conformity with the requirements of concealed wiring. | Ensure underground cables for electrical distribution in the premises, garden, compound of the building are encased in GI or PVC pipes and laid in earth trenches of sufficient depth as per BNBC. | Corrected | 12/05/2015 | On 29/05/2016 Underground service cables are found concealed . | 4/24/2015 | Corrected
4 | Cable trenches are not covered properly. | Provide adequate cover on cable trench. | Corrected | 12/05/2015 | On 29/05/2016: Corrected. On 01/09/2016: Found corrected on 1st follow-up. Also found corrected in the second. | 4/24/2015 | Corrected
5 | Emergency power distribution boards are available but not properly identified. | All boxes and enclosures (including transfer switches, generators, and power panels) for emergency circuits shall be permanently marked so they will be readily identified as a component of an emergency circuit or system. The required marking can be by color code, the words “emergency system,” or any other method that identifies the box or enclosure as a component of the emergency system. | Corrected | 02/12/2015 | On 29/05/2016: Corrected. On 01/09/2016: Found corrected on 1st follow-up. Also found corrected in the second. | 4/24/2015 | Corrected
6 | The substation room has no required fire rating or protection but is physically separated from the remainder of the building. | Provide adequate fire rating, protection for substation room. | Corrected | 12/05/2015 | On 29/05/2016 Corrected. Physically separated with fire door. On 01/09/2016: Found corrected on 1st follow-up. Also found corrected in the second. | 4/24/2015 | Corrected
7 | No additional insulation is provided for wiring exposed to external heat sources. | In order to avoid the effects of heat from external sources one of the following methods should be used to protect wiring systems: (1) shielding; (2) placing 900 mm (36 in.) from the source of heat; (3) local reinforcement or substitution of insulating material. | Corrected | 12/05/2015 | On 29/05/2016: Corrected. On 01/09/2016: Found corrected on 1st follow-up. Also found corrected in the second. | 4/24/2015 | Corrected
8 | Indications of overheating were observed in 72.1°C Note: Detail thermography report is uploaded here under general information section. | Find out the cause of overheating and take proper action including replacing cable or equipment where necessary. | Corrected | 02/12/2015 | On 29/05/2016: Corrected. On 01/09/2016: Found corrected on 1st follow-up. Also found corrected in the second. | 4/24/2015 | Corrected
9 | Bunch of cables observed at circuit breakers within distribution boards. | Remove bunch of cables at circuit breakers within distribution boards. | Corrected | 12/05/2015 | On 29/05/2016: Corrected. On 01/09/2016: Found corrected on 1st follow-up. Also found corrected in the second. | 4/24/2015 | Corrected
10 | Distribution boards are not provided with a minimum clearance of 1 m (39 in) in front. | Provide clearance of at least 1 m (39 in) in front of distribution boards. | Corrected | 12/05/2015 | On 29/05/2016: Corrected. On 01/09/2016: Found corrected on 1st follow-up. Also found corrected in the second. | 4/24/2015 | Corrected
11 | Proper Working or “as built” electrical diagram of main distribution circuit and floor levels circuits connecting electrical loads (machines/ lights/ cooling system etc.) are not available at site. The provided single line diagram was as built but no electrical layout drawing found. | Have a qualified electrical engineer develop an as-built single line diagram detailing key components and capacity of the electrical system. | Corrected | 12/05/2015 | On 29/05/2016: Corrected. On 01/09/2016: Found corrected on 1st follow-up. Also found corrected in the second. | 4/24/2015 | Corrected
12 | Thermo graphic scans of electrical equipment have not been done. | Complete thermo graphic scans at least on a three year cycle. Thermo graphic scans should be completed in accordance with the Standard for Infrared Inspection of Electrical Systems & Rotating Equipment. | Corrected | 12/05/2015 | On 29/05/2016: Corrected. On 01/09/2016: Found corrected on 1st follow-up. Also found corrected in the second. | 4/24/2015 | Corrected
13 | No periodic safety inspections of the electrical system components is completed. | Establish a periodic inspection program to ensure the electrical systems are free from damage, debris, dirt, lint, etc. Maintain records concerning inspections and follow up actions. | Corrected | 12/05/2015 | On 29/05/2016: Corrected. On 01/09/2016: Found corrected on 1st follow-up. Also found corrected in the second. | 4/24/2015 | Corrected
14 | No such information and documents found to verify the existence of harmful substances such as PCBs in transformer. | Consider replacing transformers that contain harmful substances to reduce health hazards. | Corrected | 12/05/2015 | On 29/05/2016: Corrected. On 01/09/2016: Found corrected on 1st follow-up. Also found corrected in the second. | 4/24/2015 | Corrected
15 | Distribution boards have no capacity information labels. A capacity information is provided in all distribution boards which is inadequate due to not covering all the required information. There is no indication of voltage & current capacity of the panel. | Provide capacity information labels (maximum current rating, no of circuit breakers etc.) for distribution boards. | Corrected | 12/05/2015 | On 29/05/2016: Corrected. On 01/09/2016: Found corrected on 1st follow-up. Also found corrected in the second. | 4/24/2015 | Corrected
16 | Distribution boards are not provided with physical means to prevent the installation of more over current devices than that number for which the panel board was designed, rated, and listed. | Ensure distribution boards provided with physical means to prevent the installation of more over current devices than that number for which the panel board was designed, rated, and listed. | Corrected | 12/05/2015 | On 29/05/2016: Corrected. On 01/09/2016: Found corrected on 1st follow-up. Also found corrected in the second. | 4/24/2015 | Corrected
17 | Electrical cables are not properly identified. | Ensure the means of identification is obtained by separate color coding, marking tape, tagging, or other approved means. | Corrected | 12/05/2015 | On 29/05/2016: Corrected. On 01/09/2016: Found corrected on 1st follow-up. Also found corrected in the second. | 4/24/2015 | Corrected
18 | Each circuit is not provided with a dedicated neutral. There is no marking of neutral cable in the panel. | Provide marking of neutral cable & ensure dedicated neutral for each circuit. | Corrected | 12/05/2015 | On 29/05/2016: Corrected. On 01/09/2016: Found corrected on 1st follow-up. Also found corrected in the second. | 4/24/2015 | Corrected
19 | Mechanical guards are not provided for electrical equipment. Change over switch is placed on the floor without any protection in Substation room. | Provide mechanical guards for electrical equipment where necessary. | Corrected | 02/12/2015 | On 29/05/2016: Corrected. On 01/09/2016: Found corrected on 1st follow-up. Also found corrected in the second. | 4/24/2015 | Corrected
20 | The lightning protection ground terminals are not bonded to the building or structure grounding. | Ensure lightning protection ground terminals are bonded to the building or structure grounding. | Corrected | 02/12/2015 | On 29/05/2016: Building structure was found bonded to the lightening protection ground terminal. On 01/09/2016: Found corrected on 1st follow-up. Also found corrected in the second. | 4/24/2015 | Corrected
21 | The substation room has improper illumination. | Provide additional light fixtures to increase illumination levels provided in the BNBC. | Corrected | 12/05/2015 | On 29/05/2016: Corrected. On 01/09/2016: Found corrected on 1st follow-up. Also found corrected in the second. | 4/24/2015 | Corrected
22 | The substation room is not secured properly. | Install security measures to ensure access to the substation is restricted. | Corrected | 12/05/2015 | On 29/05/2016: Corrected. On 01/09/2016: Found corrected on 1st follow-up. Also found corrected in the second. | 4/24/2015 | Corrected
23 | Improperly stored combustible material found beside generator. | Remove all dirt, debris, lint, water, oil, and improperly stored materials from the substation room. | Corrected | 12/05/2015 | On 29/05/2016: Corrected. On 01/09/2016: Found corrected on 1st follow-up. Also found corrected in the second. | 4/24/2015 | Corrected
24 | The substation room has inadequate ventilation. There is a single exhaust fan provided but no means for cross ventilation. | Provide means of ventilation for the substation room. Consult a qualified electrical engineer to determine the required ventilation rates based on the installed equipment. | Corrected | 12/05/2015 | On 29/05/2016: Corrected. On 01/09/2016: Found corrected on 1st follow-up. Also found corrected in the second. | 4/24/2015 | Corrected
25 | Cable sockets are not provided for stranded conductors. | Provide cable sockets for stranded conductors having a nominal cross-sectional area 6mm2 or greater. Conductors below 6 mm2 without cable sockets, all strands at the exposed ends are soldered together or are crimped using suitable sleeve or ferrules. | Corrected | 12/05/2015 | On 29/05/2016: Corrected. On 01/09/2016: Found corrected on 1st follow-up. Also found corrected in the second. | 4/24/2015 | Corrected
26 | Improper cable joints were found. | Ensure cable joints through porcelain, PVC connectors with PIB tape wound around joint. | Corrected | 12/05/2015 | On 29/05/2016: Corrected. On 01/09/2016: Found corrected on 1st follow-up. Also found corrected in the second. | 4/24/2015 | Corrected
27 | The electrical switchgear and panel boards are not inspected on an annual basis to ensure that the equipment is installed in accordance with the listed ratings. A checklist of inspection is maintained for all electrical switchgear and panels which is inadequate due to not covering all the required information. | Inspect electrical switchgear and panel boards on an annual basis to ensure that the equipment is in good working condition. | Corrected | 30/06/2015 | On 29/05/2016: Corrected. On 01/09/2016: Found corrected on 1st follow-up. Also found corrected in the second. | 4/24/2015 | Corrected
28 | Generator frame earthing is not provided at two separate points. Single point earthing is provided. | Provide two separate points frame earthing for generator. | Corrected | 12/05/2015 | On 29/05/2016: Corrected. On 01/09/2016: Found corrected on 1st follow-up. Also found corrected in the second. | 4/24/2015 | Corrected
29 | No periodical Insulation Resistance Measurement Program established. A record of insulation resistance test found conducted by the factory owned machine. | Develop an Insulation Resistance Measurement Program that ensures deterioration of insulation resistance will be identified quickly. Testing should be in compliance with International Electrical Testing Association (NETA). All transformers, switchgears etc. shall be subject to an insulation resistance measurement test to ground after installation but before any wiring is connected. Insulation tests shall be made between open contacts of circuit breakers, switches etc. and between each phase and earth. | Corrected | 12/05/2015 | On 29/05/2016: Corrected. On 01/09/2016: Found corrected on 1st follow-up. Also found corrected in the second. | 4/24/2015 | Corrected
30 | Internal components of distribution boards are not properly concealed. Panel bottom has opening in SDB/Dinning Room, Ground Floor. | Provide covers or blanks to conceal all live internal components of switchboards and/or distribution boards. | Corrected | 02/12/2015 | On 29/05/2016: Corrected. On 01/09/2016: Found corrected on 1st follow-up. Also found corrected in the second. | 4/24/2015 | Corrected
31 | Electrical cable is not properly terminated. | Ensure all electrical cable properly terminated at its point of termination. | Corrected | 12/05/2015 | On 29/05/2016: Corrected. On 01/09/2016: Found corrected on 1st follow-up. Also found corrected in the second. | 4/24/2015 | Corrected
32 | Electrical connections at fixtures are not properly secured. | Ensure electrical connections at equipment, fixtures, etc. are properly secured. | Corrected | 02/12/2015 | On 29/05/2016: Corrected. On 01/09/2016: Found corrected on 1st follow-up. Also found corrected in the second. | 4/24/2015 | Corrected
33 | Junction boxes are not provided with adequate covers. | Provide adequate covers for junction boxes and other electrical devices. | Corrected | 12/05/2015 | On 29/05/2016: Corrected. No such issue has been found during follow-up inspection. On 01/09/2016: Found corrected on 1st follow-up. Also found corrected in the second. | 4/24/2015 | Corrected
34 | Electrical wiring and conduit is not properly supported. | Provide adequate supports for electrical wiring and conduit. | Corrected | 02/12/2015 | On 29/05/2016: Corrected. On 01/09/2016: Found corrected on 1st follow-up. Also found corrected in the second. | 4/24/2015 | Corrected
35 | No signage indicating the prohibition of light fixtures without protective covers is installed at required locations. | Light fixtures without protective covers (otherwise known as naked lights) shall not be allowed in storage areas or in any area where the Inspector of the Factories Rules disallows these fixtures. Install signs posted in Bengali and English, indicating this prohibition at all entrances to these areas. | Corrected | 12/05/2015 | On 29/05/2016: Corrected. On 01/09/2016: Found corrected on 1st follow-up. Also found corrected in the second. | 4/24/2015 | Corrected
36 | Transformer oil analysis is not completed on main service transformers. | Complete an oil analysis on applicable transformers at appropriate intervals based on voltage and power. | Corrected | 12/05/2015 | On 29/05/2016: Corrected. On 01/09/2016: Found corrected on 1st follow-up. Also found corrected in the second. | 4/24/2015 | Corrected
37 | Equipment safety signage is not posted within the room properly. | Indoor electrical installations that are accessible to unqualified persons shall be made with metal-enclosed equipment. Switchgear, unit substations, transformers, pull boxes, connection boxes, and other similar associated equipment shall be marked with appropriate caution signs. Entrances to rooms and other guarded locations that contain exposed live parts shall be marked with conspicuous warning signs forbidding unqualified persons to enter. Caution, warning, danger signs or labels should meet the following requirements: (1) The marking shall adequately warn of the hazard using effective words and/or colors and/or symbols. American National Standards Institute ANSI Z535.4-2011, Product Safety Signs and Labels, provides guidelines for suitable font sizes, words, colors, symbols, and location requirements for labels. (2) Shall be permanently affixed to the equipment or wiring method and shall not be hand written. Exception, portions of labels or markings that are variable, or that could be subject to changes, shall be permitted to be hand written and shall be legible. (3) The label shall be of sufficient durability to withstand the environment involved. ANSI Z535.4-2011, Product Safety Signs and Labels, provides guidelines for the design and durability of safety signs and labels for application to electrical equipment. | Corrected | 12/05/2015 | On 29/05/2016: Corrected. On 01/09/2016: Found corrected on 1st follow-up. Also found corrected in the second. | 4/24/2015 | Corrected
38 | Phase separators are not provided between terminals on circuit breakers. | Install phase separators between terminal connections. Verify phase separators are installed at all remaining locations. | Corrected | 12/05/2015 | On 29/05/2016: Corrected. On 01/09/2016: Found corrected on 1st follow-up. Also found corrected in the second. | 4/24/2015 | Corrected
39 | Inspection, maintenance being completed but testing procedures of the emergency generator are not being completed. | Establish a routine maintenance and testing program for the emergency generator. The program shall be based on all of the following: (1) Manufacturer's recommendations (2) Manufacturer's Instruction manuals | Corrected | 12/05/2015 | On 29/05/2016: Corrected. On 01/09/2016: Found corrected on 1st follow-up. Also found corrected in the second. |  | Corrected
40 | New Finding: Portable generator is being used for uncertain time in a unsafe way and is placed near the main exit of the factory | Portable generator and its accessories shall be placed at a safe location to minimize hazard and the conductors for power distribution shall be protected. |  | 15/11/2016 | On 13/08/2017: Not Corrected. On 20/11/2017: Corrected. Portable generator has removed. | 2 weeks | Corrected
41 | New Finding: Air terminal are missing at several points of Lightning Protection System and baseplate is inadequate. | Missing Air Terminals shall be reinstalled and baseplate should be as per standard. |  | 25/12/2017 |  | 1 Month | In Progress
42 | New Finding: Inadequate working clearance around the generator/s | Working clearance around each generator shall be 1.07m. If multiple generators are installed, the gap between two generators must be equal to the width of the bigger one. |  | 25/12/2017 |  | 1 Month | In Progress
43 | New Finding: Cable channel/duct terminals are left open for ingression of lint, dust or fluffs. | cable ducts must be properly sealed to avoid ingression of any foreign particles. |  | 25/12/2017 |  | 1 Month | In Progress
44 | New Finding: Power sockets are hung without proper support. | Power socket has to be installed on rigid support/base securely and at minimum 200mm above floor level. |  | 25/12/2017 |  | 1 Month | In Progress
45 | New Finding: Safety program is initiated but has no influence in the factory | Electrical safety training and awareness program for the electrical personal and workers must be conducted and recorded. Training must have an impact on the safety attitude of the personnel. |  | 25/12/2017 |  | 1 Month | In Progress
46 | New Finding: Power cables entering or exiting from Distribution board/panel are not properly fixed. | Power cables entering or exiting from distribution board/panel must be fixed through Panel base/top plate using proper sized cable glands (metal/PVC). |  | 25/12/2017 |  | 1 Month | In Progress
47 | New Finding: Distribution Board's top/bottom is left open (typical issue) | Each electrical distribution board/panel must be properly sealed to avoid ingression of fluffs; but an adequate ventilation system must also be ensured. Gland shall be used, where required. |  | 25/12/2017 |  | 1 Month | In Progress
48 | New Finding: Transformer Body earthing (equipment earthing) and Neutral earthing(System earthing) cable size is inadequate Inadequate sized earth cable connected to generator frame. | Equipment earthing cable size must be increased. The earth cable size shall be less than or equal to half of the phase cable (depends on fault clearing time). You may use equivalent sized bare copper conductor. Number of earth pits shall be determined by the size of connected earth cable. Two separate earth connection & one separate and distinct Neutral connection must be provided over generator. Generator body must have earth connection with half of phase conductor. |  | 25/12/2017 |  | 1 Month | In Progress
49 | New Finding: Transformer Silica gel is discolored | Silica gel shall be changed; or reuse can be done, if color regains after sundry. |  | 25/12/2017 |  | 1 Month | In Progress
50 | New Finding: Generator output cables (laid on floor) are not protected and supported | Service cables from generator must be supported at its own breaker's terminal and with cable tray. |  | 25/12/2017 |  | 1 Month | In Progress
51 | New Finding: No working separation between LT ( Low Tension) panel/s and HT (High Tension) unit/s (Transformer, HT switchgear) and there is no proper access to transformer | A working separation between LT and HT must be ensured. A brick wall will do it; and adequate working clearance (1.07m) and ventilation must be ensured. Proper access to the transformer should ensured for maintenance. |  | 25/12/2017 |  | 1 Month | In Progress